## Summary
|  |  | STD information |  |  | Author information
|  |  | STD ID | testCIPDO |  | Written by | AdminAcc
|  |  | Version of the test sheet |  |  | Writing status | written & reviewed OK
| Version of Orchestra format |  | Project |  |  | Writing date | 2019-07-15
| v20 |  | Test stage
|  |  | Stage category |  |  | Resources required for test
|  |  | Test type |  |  | Estimate preparation duration
|  |  | Verification method (IADT) |  |  | Estimate running duration
|  |  | Applicable location(s) |  |  | Test during TH/NTH
|  |  | Test title |  |  | Number of tester(s)
|  |  | Test objective |  |  | Equipment and quantity
|  |  | Covered requirements |  |  | STD Checksum
| Legends |  | STR information |  |  | Tester information
| To be filled from list |  | System version under test |  |  | Run by | TAT
| Automatically filled |  | Test environment |  |  | Running date | 2019-07-15
| Context step |  | IO schedule version | testCIPDO
| To be filled by author |  | Instrument calibration certificate |  |  | Resources required for test
| To be filled by tester |  | Allocated location(s) |  |  | Approximate preparation duration
|  |  | Total steps | 10 |  | Approximate running duration
| Language |  | STR results |  |  | Associated defects
| En |  | Total Not Tested | 0
|  |  | Total OK | 10
|  |  | Total OKWC | 0
|  |  | Total NOK | 0
|  |  | Total Not Testable | 0 |  | Comments
|  |  | Total Out Of Scope | 0
|  |  | Test case result | 10
|  |  | Thales Signature |  |  | Customer / External Signature
|  |  | Customer / External Signature |  |  | Customer / External Signature
end | end | end | end | end | end | end | end | end
All sheets
Tester view
Author view
Automation view
Import view
Export view
Set up views
How To view
Custom view

## Views (hidden)
Configuration of the available views
Views
Sheets | Custom | Tester | Author | Import | Export | Views | HowTo | Automation
Summary | Visible | Visible | Visible | Visible | Visible | Visible | Visible | Visible
Views | [5 empty] | Visible
Procedure | Visible | Visible | Visible |  |  |  |  | Visible
User manual |  |  | Visible
defaultValues
How To |  | Visible | Visible |  |  |  | Visible
Language
Automation | [7 empty] | Visible
Export |  |  |  |  | Visible
Import |  |  |  | Visible
ToolVersion
ProcedureVersion |  |  | Visible
Result Matrix |  | Visible

## User manual (hidden)
User Manual
Fields description | View cells comments
Enumeration | Values | meaning | Description
Step State | OK | OK | The observed result is exactly as the expected result
| OKWC | OK with comment | The observed result is almost as the expected result
| NOK | Not OK | The observed result is not as the expected result
| NT | Not Testable | The step description cannot be executed
| OS | Out of scope | The step is not in the scope of the test (e.g. simulated vs real environment)
Context | X | Comment | Use this context to insert comments to the test procudre (NB: for author, not for tester)
| P | Section title | Use this context to insert a section title
Regression thread | Y | Yes | Use this if the thread test regression
| N | No | Use this if the thread not test regression
Writing Status | not written | Not written | The sheet is not written
| in progress | Being written | The sheet is not full written
| written & reviewed OK | Written & reviewed OK | The sheet review is validate
Running Status | not run | not run | The thread was never run
| in progress | being run | The thread is not run completely
| run completed | run completed | The thread was run for an attempt
IADT | I - Inspection | Inspection | The requirement is verified by examination of the product
| A - Analysis | Analysis | The requirement is verified by using model and calculation to make predictive statement of the product
| D - Demonstration | Demonstration | The requirement is verified by manipulating and examining the output product
| T - Test | Test | The requirement is verified by manipulating and measuring the output of the prodcut (if not measurable, it's a demonstration)
Validation platform | Development paltform | Development paltform | The test is meant to be executed on the development platform
| Integration platform | Integration platform | The test is meant to be executed on the integration platform
| Software proofing platform | Software proofing platform | The test is meant to be executed on the software proofing platform
| Cubicle factory | Cubicle factory | The test is meant to be executed in the cubicle factory
| On site | On site | The test is meant to be executed on site
How to customize Enumeration ?
Enumeration are store in "defaultValues" sheet.

## defaultValues (hidden)
Legend | Step state | Context | Regression | Writing Status | Running Status | TH/NTH | IADT | Validation platform | Version | System | Location | Type of test | Projects | Test stage
Do not modify | OK | X | Yes | not written | not run | TH | I - Inspection | Development paltform | V0 | AFC | HKB | Visual inspection | 1166B - SCL Phase 2 | Internal tests
Can be modify | OKWC | P | No | in progress | in progress | NTH | A - Analysis | Integration platform | V1 | AFC & SAMS | ADM | Demonstration test | 3733 - TKL | Software proofing tests
| NOK |  |  | written & reviewed OK | run completed |  | D - Demonstration | Software proofing platform | V2 | BMS | EXH | Communication test | 759 - WIL/KTE | Factory Acceptance tests
| NT | [5 empty] | T - Test | Cubicle factory | V3 | BS | SOV | Software unit test | 762 - WIL/KTE/SIL | Installation tests
| OS | [6 empty] | On site | V4 | CASS | NOV | Software integration test | 966 - SIL E | Site integration tests
[9 empty] | V5 | CDN | HUH | System integration test | DHLRT | Interface and integrated tests
[9 empty] | V6 | COM | EAP 7 | Point-to-point test | NWSL | System acceptance tests
[9 empty] | V7 | ERL PRC & BHT TVS | EAP 1-6 | End-to-end test |  | Test running
[9 empty] | V8 | FG | MKK | Functional test |  | Training System
[9 empty] | V9 | ITDN | KOT | Data applicable test |  | Other (e.g. Interfaces)
[9 empty] | V10 | LIF & ESC | TAW
[10 empty] | MCS | SHT
[10 empty] | MCS (CMCS_SMS) | HTD
[10 empty] | MCS (DBMS) | FOT
[10 empty] | MCS (DSS) | RAC
[10 empty] | MCS (E.Sign PLC) | UNI
[10 empty] | MCS (FEP) | TAD
[10 empty] | MCS (Field PLC) | TAP
[10 empty] | MCS (IBP) | TWO
[10 empty] | MCS (PRC PLC) | FAN
[10 empty] | MCS (SDS) | SHS
[10 empty] | MCS (TSS) | LOW
[10 empty] | MIMIC | CTV
[10 empty] | Misc | SSV
[10 empty] | MMIS | LMC
[10 empty] | OHL | OCC
PMW
POW
PSD & APG
RAD
RS
SIG
TECS
TETRA
TGMS
TODS
UITS
URL PRC

## Language (hidden)
En | Fr | Ch | Value
0
Language | Langue |  | Language
0
STD information | Information du STD |  | STD information
STD ID | ID du STD | 测试表格编号 | STD ID
Version of the test sheet | Version de la fiche de test |  | Version of the test sheet
Project | Projet |  | Project
Test type | Type de test |  | Test type
Test stage | Phase de test | 测试阶段 | Test stage
Stage category | Catégorie de la phase de test |  | Stage category
Verification method (IADT) | Méthode de vérification (IADT) |  | Verification method (IADT)
Resources required for test | Ressources nécéssaires pour le test |  | Resources required for test
Estimate preparation duration | Durée estimée de préparation |  | Estimate preparation duration
Estimate running duration | Durée estimée d'exécution |  | Estimate running duration
Test during TH/NTH | Test pendant TH/NTH |  | Test during TH/NTH
Number of tester(s) | Nombre de testeur(s) |  | Number of tester(s)
Equipment and quantity | Equipement et quantité |  | Equipment and quantity
Applicable location(s) | Localisation(s) applicable(s) |  | Applicable location(s)
Test title | Titre du Test | 测试标题 | Test title
Test objective | Objectif du test | 测试目的 | Test objective
0
Author information | Informations sur l'auteur |  | Author information
Written by | Rédacteur |  | Written by
Writter email | Adresse mail du rédacteur |  | Writter email
Writing status | Etat de l'écriture |  | Writing status
Writing date | Date d'écriture |  | Writing date
0
STD Checksum | Checksum du STD |  | STD Checksum
0
Covered requirements | Exigence couvertes |  | Covered requirements
0
STR information | Information du STR |  | STR information
System version under test | Version systeme testée | 软件版本 | System version under test
Test environment | Environnement de test |  | Test environment
IO schedule version | Version de l'IO list | I/O定义版本 | IO schedule version
Termination schedule version | Version du termination schedule |  | Termination schedule version
Allocated location(s) | Localisation(s) appliquée(s) |  | Allocated location(s)
Total steps | Total pas |  | Total steps
0
Tester information | Informations sur le testeur |  | Tester information
Run by | Testeur |  | Run by
Runner email | Adresse mail du testeur |  | Runner email
Running date | Date de l'exécution |  | Running date
Approximate preparation duration | Durée approximative de préparation |  | Approximate preparation duration
Approximate running duration | Durée approximative d'exécution |  | Approximate running duration
Instrument calibration certificate | Certificat de calibration des instruments |  | Instrument calibration certificate
0
STR results | Resultats du STR |  | STR results
Total Not Tested | Total pas restants |  | Total Not Tested
Total OK | Total OK |  | Total OK
Total OKWC | Total OKWC |  | Total OKWC
Total NOK | Total NOK |  | Total NOK
Total Not Testable | Total Non Testable |  | Total Not Testable
Total Out Of Scope | Total Hors Scope |  | Total Out Of Scope
Test case result | Resultat du cas de test | 测试结果 | Test case result
0
STR metrics | Métriques du STR |  | STR metrics
% Not Tested | % pas restants |  | % Not Tested
% OK | % OK |  | % OK
% OKWC | % OKWC |  | % OKWC
% NOK | % NOK |  | % NOK
% Not Testable | % Non Testable |  | % Not Testable
% Out Of Scope | % Hors Scope |  | % Out Of Scope
Number of test steps with defect | Nombre de pas de test avec défaut |  | Number of test steps with defect
0
Number of test cases | Nombre de cas de test |  | Number of test cases
Number of test cases for regression | Nombre de cas de test de non régression |  | Number of test cases for regression
Number of test cases in live session | Nombre de cas de test en "live session" |  | Number of test cases in live session
0
Last run date | Date de dernière exécution |  | Last run date
% OK | % OK |  | % OK
System version under test | Version systeme testée |  | System version under test
Software test environment | Environnement de test logiciel |  | Software test environment
Hardware test environment | Environnement de test matériel |  | Hardware test environment
0
To be filled from list | A remplir depuis une liste |  | To be filled from list
Automatically filled | Rempli automatiquement |  | Automatically filled
To let empty | A laisser vide |  | To let empty
Context step | Pas de contexte |  | Context step
To be filled by author | A remplir par l'auteur |  | To be filled by author
To be filled by tester | A remplir par le testeur |  | To be filled by tester
0
Test case description | Description du cas de test |  | Test case description
Regression | Non régression |  | Regression
Validation platform | Plateforme de validation |  | Validation platform
Tester name | Nom du testeur |  | Tester name
Last test date | Date de dernière execution |  | Last test date
0
Test case id | Identifiant du cas de test |  | Test case id
Context | Contexte |  | Context
Step # | Pas de test # |  | Step #
Step description | Description du pas de test | 输入/动作 | Step description
Expected result | Résultat attendu | 预期结果 | Expected result
Verification type | Type de vérification |  | Verification type
Last state date | Date de dernière exécution | 日期 | Last state date
Tester | Testeur | 测试人 | Tester
Result | Résultat |  | Result
Associated defect (PCR ID) | Défaut associé |  | Associated defect (PCR ID)
Comment on result | Commentaire sur le résultat |  | Comment on result
Historic defects | Défauts associés précédemment |  | Historic defects
Requirement | Exigence attachée |  | Requirement
Free column | Colonne libre |  | Free column
Test case result | Resultat du cas de test |  | Test case result
0
Passed | Passé |  | Passed
Failed | Manqué |  | Failed
Blocked | Bloqué |  | Blocked
Error | Erreur |  | Error
Inconclusive | Non concluant |  | Inconclusive
0
Test state | Etat du test |  | Test state
0
Legends | Légendes |  | Legends
0
Yes | Oui |  | Yes
No | Non |  | No
Comments | Commentaires | 意见 | Comments
Remedial work | Action corrective |  | Remedial work
Steps tested on last run date | Pas testés lors de dernière exécution |  | Steps tested on last run date
Associated defects | Défauts associés |  | Associated defects
Customer / External Signature | Client / Externe Signature |  | Customer / External Signature
Thales Signature | Thales Signature |  | Thales Signature
Instance of the test sheet execution | Instance d'éxécution |  | Instance of the test sheet execution
Test sheet Source | Source STD |  | Test sheet Source
Number of test steps OKWC or NOK without PCR | Total pas de tests NOK ou OKWC sans PCR |  | Number of test steps OKWC or NOK without PCR
Total requirements NOK | Total des exigences NOK |  | Total requirements NOK
Traceability | Tracabilité |  | Traceability
Controls on the inputs | Controles des données insérées |  | Controls on the inputs
Information | Information |  | Information
Number of test steps OS without comments | Total Hors Scope sans commentaire |  | Number of test steps OS without comments
Duration for STD preparation | Durée pour la préparation du STD |  | Duration for STD preparation
Requirement Source Version | Version des exigences |  | Requirement Source Version
0
Notes | Notes |  | Notes
0
Version of Orchestra format | Version du format Orchestra |  | Version of Orchestra format
0
0
0
0
0
0
0

## Automation (hidden)
Configuration to create Automation Script to a Word Document
Target
Directory
Template
Files for the import to create the script
ID | New File ? | New Name | File Source | Free Field 1 | Free Field 2 | Free Field 3 | Free Field 4 | Free Field 5
Import General Data
Source of Import |  |  |  |  | Word Target Document based on template selected
Data name | Type | Table Id or Value | Line | Column | Field name | Table ID | Line | Column

## Export (hidden)
Configuration to export to a Word Document
Target
Directory
Template
Files for the import
ID | New File ? | New Name | File Source | Free Field 1 | Free Field 2 | Free Field 3 | Free Field 4 | Free Field 5
end
end
end
end
end
end
end
end
end
end
Import General Data
Source of Import based on Orchestra template |  |  |  |  | Word Target Document based on template selected
Data name | Type | Table Id or Value | Line | Column | Field name | Table ID | Line | Column
Test sheet identification | Value from Excel | Summary | 3 | 5 | Test sheet identification | 1 | 1 | 2
Test sheet version | Value from Excel | Summary | 4 | 5 | Test sheet version | 1 | 1 | 3
Attendee | Value | 966 MCS, MTR | 24 | 8 | Attendee | 1 | 1 | 5
Test Title | Value from Excel | Summary | 9 | 5 | Test Title | 1 | 2 | 2
Purpose of the test | Value from Excel | Summary | 10 | 5 | Purpose of the test | 1 | 2 | 4
Test phase | Value from Excel | Summary | 6 | 5 | Test Phase | 2 | 1 | 2
Configuration | Value from Excel | Summary | 14 | 5 | Configuration | 2 | 1 | 4
Location of test | Value | TT&S HK Office |  |  | Location of test | 2 | 2 | 2
Instrument calibration date | Value |  |  |  | Instrument calibration date | 2 | 2 | 4
System version | Value from Excel | Summary | 13 | 5 | System version | 3 | 1 | 2
Test id | Value from Excel | Summary | 3 | 5 | Test id | 4 | 1 | 1
Test id | Value from Excel | Summary | 3 | 5 | Test id | 5 | 1 | 1
Import Steps
Source for import |  |  |  |  | Word Target Document based on template selected
Starting line | LatestRun | Starting line | 17 |  | Template Line | 4 | Starting line | 3
Data name | Type | Sheet Name, Table, value or formula | Starting Line | Column | Field name | Table ID | Starting Line | Column
Step Number | Value from Excel | LatestRun | 17 | 2 | Step Number | 4 | 3 | 1
Step description | Value from Excel | LatestRun | 17 | 3 | Step description | 4 | 3 | 2
Expected result | Value from Excel | LatestRun | 17 | 4 | Expected result | 4 | 3 | 3
Verification type | Not exported | LatestRun | 17 | 5 | Verification type | 4 | 3 | 0
OK | Value | [ ] | 17 | 6 | OK | 4 | 3 | 4
OKWC | Value | [ ] | 17 |  | OKWC | 4 | 3 | 6
NOK | Value | [ ] | 17 |  | NOK | 4 | 3 | 5
Associated defect | Value from Excel | LatestRun | 17 | 7 | PCR | 4 | 3 | 7
Comment | Value from Excel | LatestRun | 17 | 8 | Comment | 4 | 3 | 8
Export to Word

## Import (hidden)
Configuration to import data from a file to this Excel Test Sheet - Matrix of applicability
Target
Directory
Files for the import | [19 empty] | Log
|  |  |  | FreeField 1 | FreeField 2 | FreeField 3 | FreeField 4 | FreeField 5 | FreeField 6 | FreeField 7 | FreeField 8 | FreeField 9 | FreeField 10 | FreeField 11 | FreeField 12 | FreeField 13 | FreeField 14 | FreeField 15 | FreeField 16
ID | New File Name | File Location | Template | STD ID | Test title | Not used | Not used | Not used | Not used | Not used | Not used | Not used | Not used | Not used | Not used | Not used | Not used | Not used | Not used | Start Update at : 14:45:37 | Nb Steps
Import General Data
Source for import |  |  |  |  | Target in Orchestra STD
Data name | Type | Sheet Name, Table, value or formula | Line | Column | Field name | Sheet Name | Line | Column
Category of test | Value from File Free Field | FreeField4 |  |  | Category of test | Summary | 7 | 5
Location | Value from File Free Field | FreeField5 |  |  | Location | Summary | 8 | 5
Regression thread | Value | No |  |  | Regression thread | Summary | 3 | 8
Cubicle ID | Value from File Free Field | FreeField1 |  |  | Instance of the test sheet execution | Summary | 23 | 8
Cubicle ID | Value from File Free Field | FreeField1 |  |  | Cubicle ID | Summary | 19 | 5
System | Value | System |  |  | System Label | Summary | 19 | 7
System | Value from File Free Field | FreeField3 |  |  | System | Summary | 19 | 8
Room | Value | Room |  |  | Label Room | Summary | 20 | 7
Room | Value from File Free Field | FreeField6 |  |  | Room | Summary | 20 | 8
Import Steps
Source for import |  |  |  |  | Target in Orchestra STD
Data name | Type | Sheet Name, Table, value or formula | Starting Line | Column | Field name | Sheet Name | Starting Line | Column
Generate STD

## ToolVersion (hidden)
Version | Date | Responsible | Comments
v01 | - | Group Thales | Version 4.2.1 From Orchestra
v02 | 2014-02-12 | D. Castilla
v03 |  | D. Castilla
v04 |  | D. Castilla
v05 |  | D. Castilla
v06 | 2014-02-19 | D. Castilla | Clean the VBA code
v07 | 2014-02-20 | D. Castilla | Clean the VBA code
v08 | 2014-02-21 | D. Castilla | Clean the VBA code
v09 | 2014-02-22 | D. Castilla | Clean the VBA code
v10 | 2014-04-06 | D. Castilla | Improve the Summary organization
v11 | 2014-04-12 | D. Castilla | Optimize the function Import to be able to link each file with a specific template. + Add legend in the summary to explain the Stat of result
v12
v13
v14 | 2014-07-19 | D. Castilla & J. Ng | Export function from Excel to Word Add Duration for Preparation Field
v15 | 2014-07-29 | D. Castilla & J. Ng | Add Requirement Version in the Summary Sheet
v16 | 2016-02-05 | D. Castilla & C. Rousseau | - Add ProcedureVersion sheet to track the changes in the content of the STD (the field Test case version is now automatically computed based on the content of this tab) - Delete Project Compliance sheet - Reworked summary (add/removed fields, added color to differenciate to be filled by author/tester) - Reworked language (re-order to match order in summary sheet) - Reworked User manual (remove images, re-wrote the meaning of enumerations, etc.)
v17 | 2016-02-17 | C. Rousseau | - Add Result Matrix sheet - Reworked summary - Add chinese language - Add checksum functionality
v18 | 2016-03-29 | C. Rousseau | Updated the formula in the tab Language, such that Excel will not ask anymore to save the file on closure when the file has not been modified
v19 | 2016-03-31 | C. Rousseau | Add back the Test Category
v20 | 2016-05-31 | C. Rousseau | - Updated the format to have a better contrast for B&W printing - Updated the Import function to support up to 16 free fields

## ProcedureVersion (hidden)
Version | Date | Responsible | Comments
v01 | 2016-07-04 | Peter CHAN | Creation

## Result Matrix (hidden)
Steps
|  | Total Out Of Scope | Total OK | Total OKWC | Total NOK | Total Not Tested | Total Not Testable
Cases | NT | allowed | 0 | 0 | 0 | 100% | 0
| OS | 100% | 0 | 0 | 0 | 0 | 0
| Incomplete | allowed | at least 1 |  | 0 | at least 1
| NTestable | allowed | 0 | 0 | 0 | 0 | 100%
| NOK | allowed | allowed | allowed | at least 1 | allowed | allowed
| OKWC | allowed | allowed | at least 1 | 0 | 0 | 0
| OK | allowed | 100% | 0 | 0 | 0 | 0

## Report
Station | Eqpt_Code | Eqpt_Description(MCS) | Eqpt_Identifier | Attribute_Description(MCS) | DC_Data_Type | v0_label(1) | v0_Severity | v0_State | v1_label(2) | v1_Severity | v1_State | v2_label(3) | v2_Severity | v2_State | v3_label(4) | v3_Severity | v3_State | v4_label(5) | v4_Severity | v4_State | v5_label(6) | v5_Severity | v5_State | v6_label(7) | v6_Severity | v6_State | v7_label(8) | v7_Severity | v7_State | Program Tag | Full Tag | Result | Associated defect (PCR ID) | Comment on result | System version under test | Date | Tester
LGD | SMP_ | Tunnel Drainage Sump | SMP172 | Alarm Reset Command | CIPDO | N/A |  |  | N/A |  |  | N/A |  |  | N/A |  |  | N/A |  |  | N/A |  |  | Reset |  |  | N/A |  |  | SMP172 | SMP172_SI.AlarmResetCmd | OK |  | Link to Raw Result |  | 2019-07-15 | TAT
LGD | DPP_ | Tunnel Drainage Pump | DPP321 | Alarm Reset Command | CIPDO | N/A |  |  | N/A |  |  | N/A |  |  | N/A |  |  | N/A |  |  | N/A |  |  | Reset |  |  | N/A |  |  | SMP172 | DPP321_SI.AlarmResetCmd | OK |  | Link to Raw Result |  | 2019-07-15 | TAT
LGD | DPP_ | Tunnel Drainage Pump | DPP321 | Availability Command | CIPDO | N/A |  |  | N/A |  |  | N/A |  |  | N/A |  |  | N/A |  |  | Out Of Service |  |  | In Service |  |  | N/A |  |  | SMP172 | DPP321_SI.AvailabilityCmd | OK |  | Link to Raw Result |  | 2019-07-15 | TAT
LGD | DPP_ | Tunnel Drainage Pump | DPP321 | Control Mode Command | CIPDO | N/A |  |  | N/A |  |  | N/A |  |  | N/A |  |  | N/A |  |  | Remote Manual |  |  | Remote Auto |  |  | N/A |  |  | SMP172 | DPP321_SI.ControlModeCmd | OK |  | Link to Raw Result |  | 2019-07-15 | TAT
LGD | DPP_ | Tunnel Drainage Pump | DPP321 | Operational State Command | CIPDO | N/A |  |  | N/A |  |  | N/A |  |  | N/A |  |  | N/A |  |  | Run |  |  | Stop |  |  | N/A |  |  | SMP172 | DPP321_SI.OpStateCmd | OK |  | Link to Raw Result |  | 2019-07-15 | TAT
LGD | DPP_ | Tunnel Drainage Pump | DPP321 | Reset Hours Run Command | CIPDO | N/A |  |  | N/A |  |  | N/A |  |  | N/A |  |  | N/A |  |  | N/A |  |  | Reset |  |  | N/A |  |  | SMP172 | DPP321_SI.ResetHoursRunCmd | OK |  | Link to Raw Result |  | 2019-07-15 | TAT
LGD | DPP_ | Tunnel Drainage Pump | DPP322 | Alarm Reset Command | CIPDO | N/A |  |  | N/A |  |  | N/A |  |  | N/A |  |  | N/A |  |  | N/A |  |  | Reset |  |  | N/A |  |  | SMP172 | DPP322_SI.AlarmResetCmd | OK |  | Link to Raw Result |  | 2019-07-15 | TAT
LGD | DPP_ | Tunnel Drainage Pump | DPP322 | Availability Command | CIPDO | N/A |  |  | N/A |  |  | N/A |  |  | N/A |  |  | N/A |  |  | Out Of Service |  |  | In Service |  |  | N/A |  |  | SMP172 | DPP322_SI.AvailabilityCmd | OK |  | Link to Raw Result |  | 2019-07-15 | TAT
LGD | DPP_ | Tunnel Drainage Pump | DPP322 | Control Mode Command | CIPDO | N/A |  |  | N/A |  |  | N/A |  |  | N/A |  |  | N/A |  |  | Remote Manual |  |  | Remote Auto |  |  | N/A |  |  | SMP172 | DPP322_SI.ControlModeCmd | OK |  | Link to Raw Result |  | 2019-07-15 | TAT
LGD | DPP_ | Tunnel Drainage Pump | DPP322 | Operational State Command | CIPDO | N/A |  |  | N/A |  |  | N/A |  |  | N/A |  |  | N/A |  |  | Run |  |  | Stop |  |  | N/A |  |  | SMP172 | DPP322_SI.OpStateCmd | OK |  | Link to Raw Result |  | 2019-07-15 | TAT

## Raw Result
Overall Result | EventList Result | Data Type | Program Tag | Full Tag | Triggering State | Station |  | EQP Code |  | EQP Number |  | EQP Description |  | Attribute Description |  | State
[6 empty] | Searched | Found | Searched | Found | Searched | Found | Searched | Found | Searched | Found | Searched | Found
OK
| OS | CIPDO | SMP172 | SMP172_SI.AlarmResetCmd | 0 | LGD | N/A | SMP_ | N/A | SMP172 | N/A | Tunnel Drainage Sump | N/A | Alarm Reset Command | N/A | N/A | N/A
| OS | CIPDO | SMP172 | SMP172_SI.AlarmResetCmd | 1 | LGD | N/A | SMP_ | N/A | SMP172 | N/A | Tunnel Drainage Sump | N/A | Alarm Reset Command | N/A | N/A | N/A
| OS | CIPDO | SMP172 | SMP172_SI.AlarmResetCmd | 2 | LGD | N/A | SMP_ | N/A | SMP172 | N/A | Tunnel Drainage Sump | N/A | Alarm Reset Command | N/A | N/A | N/A
| OS | CIPDO | SMP172 | SMP172_SI.AlarmResetCmd | 3 | LGD | N/A | SMP_ | N/A | SMP172 | N/A | Tunnel Drainage Sump | N/A | Alarm Reset Command | N/A | N/A | N/A
| OS | CIPDO | SMP172 | SMP172_SI.AlarmResetCmd | 4 | LGD | N/A | SMP_ | N/A | SMP172 | N/A | Tunnel Drainage Sump | N/A | Alarm Reset Command | N/A | N/A | N/A
| OS | CIPDO | SMP172 | SMP172_SI.AlarmResetCmd | 5 | LGD | N/A | SMP_ | N/A | SMP172 | N/A | Tunnel Drainage Sump | N/A | Alarm Reset Command | N/A | N/A | N/A
| OK | CIPDO | SMP172 | SMP172_SI.AlarmResetCmd | 6 | LGD | N/A | SMP_ | N/A | SMP172 | N/A | Tunnel Drainage Sump | N/A | Alarm Reset Command | N/A | Reset | N/A
| OS | CIPDO | SMP172 | SMP172_SI.AlarmResetCmd | 7 | LGD | N/A | SMP_ | N/A | SMP172 | N/A | Tunnel Drainage Sump | N/A | Alarm Reset Command | N/A | N/A | N/A
OK
| OS | CIPDO | SMP172 | DPP321_SI.AlarmResetCmd | 0 | LGD | N/A | DPP_ | N/A | DPP321 | N/A | Tunnel Drainage Pump | N/A | Alarm Reset Command | N/A | N/A | N/A
| OS | CIPDO | SMP172 | DPP321_SI.AlarmResetCmd | 1 | LGD | N/A | DPP_ | N/A | DPP321 | N/A | Tunnel Drainage Pump | N/A | Alarm Reset Command | N/A | N/A | N/A
| OS | CIPDO | SMP172 | DPP321_SI.AlarmResetCmd | 2 | LGD | N/A | DPP_ | N/A | DPP321 | N/A | Tunnel Drainage Pump | N/A | Alarm Reset Command | N/A | N/A | N/A
| OS | CIPDO | SMP172 | DPP321_SI.AlarmResetCmd | 3 | LGD | N/A | DPP_ | N/A | DPP321 | N/A | Tunnel Drainage Pump | N/A | Alarm Reset Command | N/A | N/A | N/A
| OS | CIPDO | SMP172 | DPP321_SI.AlarmResetCmd | 4 | LGD | N/A | DPP_ | N/A | DPP321 | N/A | Tunnel Drainage Pump | N/A | Alarm Reset Command | N/A | N/A | N/A
| OS | CIPDO | SMP172 | DPP321_SI.AlarmResetCmd | 5 | LGD | N/A | DPP_ | N/A | DPP321 | N/A | Tunnel Drainage Pump | N/A | Alarm Reset Command | N/A | N/A | N/A
| OK | CIPDO | SMP172 | DPP321_SI.AlarmResetCmd | 6 | LGD | N/A | DPP_ | N/A | DPP321 | N/A | Tunnel Drainage Pump | N/A | Alarm Reset Command | N/A | Reset | N/A
| OS | CIPDO | SMP172 | DPP321_SI.AlarmResetCmd | 7 | LGD | N/A | DPP_ | N/A | DPP321 | N/A | Tunnel Drainage Pump | N/A | Alarm Reset Command | N/A | N/A | N/A
OK
| OS | CIPDO | SMP172 | DPP321_SI.AvailabilityCmd | 0 | LGD | N/A | DPP_ | N/A | DPP321 | N/A | Tunnel Drainage Pump | N/A | Availability Command | N/A | N/A | N/A
| OS | CIPDO | SMP172 | DPP321_SI.AvailabilityCmd | 1 | LGD | N/A | DPP_ | N/A | DPP321 | N/A | Tunnel Drainage Pump | N/A | Availability Command | N/A | N/A | N/A
| OS | CIPDO | SMP172 | DPP321_SI.AvailabilityCmd | 2 | LGD | N/A | DPP_ | N/A | DPP321 | N/A | Tunnel Drainage Pump | N/A | Availability Command | N/A | N/A | N/A
| OS | CIPDO | SMP172 | DPP321_SI.AvailabilityCmd | 3 | LGD | N/A | DPP_ | N/A | DPP321 | N/A | Tunnel Drainage Pump | N/A | Availability Command | N/A | N/A | N/A
| OS | CIPDO | SMP172 | DPP321_SI.AvailabilityCmd | 4 | LGD | N/A | DPP_ | N/A | DPP321 | N/A | Tunnel Drainage Pump | N/A | Availability Command | N/A | N/A | N/A
| OK | CIPDO | SMP172 | DPP321_SI.AvailabilityCmd | 5 | LGD | N/A | DPP_ | N/A | DPP321 | N/A | Tunnel Drainage Pump | N/A | Availability Command | N/A | Out Of Service | N/A
| OK | CIPDO | SMP172 | DPP321_SI.AvailabilityCmd | 6 | LGD | N/A | DPP_ | N/A | DPP321 | N/A | Tunnel Drainage Pump | N/A | Availability Command | N/A | In Service | N/A
| OS | CIPDO | SMP172 | DPP321_SI.AvailabilityCmd | 7 | LGD | N/A | DPP_ | N/A | DPP321 | N/A | Tunnel Drainage Pump | N/A | Availability Command | N/A | N/A | N/A
OK
| OS | CIPDO | SMP172 | DPP321_SI.ControlModeCmd | 0 | LGD | N/A | DPP_ | N/A | DPP321 | N/A | Tunnel Drainage Pump | N/A | Control Mode Command | N/A | N/A | N/A
| OS | CIPDO | SMP172 | DPP321_SI.ControlModeCmd | 1 | LGD | N/A | DPP_ | N/A | DPP321 | N/A | Tunnel Drainage Pump | N/A | Control Mode Command | N/A | N/A | N/A
| OS | CIPDO | SMP172 | DPP321_SI.ControlModeCmd | 2 | LGD | N/A | DPP_ | N/A | DPP321 | N/A | Tunnel Drainage Pump | N/A | Control Mode Command | N/A | N/A | N/A
| OS | CIPDO | SMP172 | DPP321_SI.ControlModeCmd | 3 | LGD | N/A | DPP_ | N/A | DPP321 | N/A | Tunnel Drainage Pump | N/A | Control Mode Command | N/A | N/A | N/A
| OS | CIPDO | SMP172 | DPP321_SI.ControlModeCmd | 4 | LGD | N/A | DPP_ | N/A | DPP321 | N/A | Tunnel Drainage Pump | N/A | Control Mode Command | N/A | N/A | N/A
| OK | CIPDO | SMP172 | DPP321_SI.ControlModeCmd | 5 | LGD | N/A | DPP_ | N/A | DPP321 | N/A | Tunnel Drainage Pump | N/A | Control Mode Command | N/A | Remote Manual | N/A
| OK | CIPDO | SMP172 | DPP321_SI.ControlModeCmd | 6 | LGD | N/A | DPP_ | N/A | DPP321 | N/A | Tunnel Drainage Pump | N/A | Control Mode Command | N/A | Remote Auto | N/A
| OS | CIPDO | SMP172 | DPP321_SI.ControlModeCmd | 7 | LGD | N/A | DPP_ | N/A | DPP321 | N/A | Tunnel Drainage Pump | N/A | Control Mode Command | N/A | N/A | N/A
OK
| OS | CIPDO | SMP172 | DPP321_SI.OpStateCmd | 0 | LGD | N/A | DPP_ | N/A | DPP321 | N/A | Tunnel Drainage Pump | N/A | Operational State Command | N/A | N/A | N/A
| OS | CIPDO | SMP172 | DPP321_SI.OpStateCmd | 1 | LGD | N/A | DPP_ | N/A | DPP321 | N/A | Tunnel Drainage Pump | N/A | Operational State Command | N/A | N/A | N/A
| OS | CIPDO | SMP172 | DPP321_SI.OpStateCmd | 2 | LGD | N/A | DPP_ | N/A | DPP321 | N/A | Tunnel Drainage Pump | N/A | Operational State Command | N/A | N/A | N/A
| OS | CIPDO | SMP172 | DPP321_SI.OpStateCmd | 3 | LGD | N/A | DPP_ | N/A | DPP321 | N/A | Tunnel Drainage Pump | N/A | Operational State Command | N/A | N/A | N/A
| OS | CIPDO | SMP172 | DPP321_SI.OpStateCmd | 4 | LGD | N/A | DPP_ | N/A | DPP321 | N/A | Tunnel Drainage Pump | N/A | Operational State Command | N/A | N/A | N/A
| OK | CIPDO | SMP172 | DPP321_SI.OpStateCmd | 5 | LGD | N/A | DPP_ | N/A | DPP321 | N/A | Tunnel Drainage Pump | N/A | Operational State Command | N/A | Run | N/A
| OK | CIPDO | SMP172 | DPP321_SI.OpStateCmd | 6 | LGD | N/A | DPP_ | N/A | DPP321 | N/A | Tunnel Drainage Pump | N/A | Operational State Command | N/A | Stop | N/A
| OS | CIPDO | SMP172 | DPP321_SI.OpStateCmd | 7 | LGD | N/A | DPP_ | N/A | DPP321 | N/A | Tunnel Drainage Pump | N/A | Operational State Command | N/A | N/A | N/A
OK
| OS | CIPDO | SMP172 | DPP321_SI.ResetHoursRunCmd | 0 | LGD | N/A | DPP_ | N/A | DPP321 | N/A | Tunnel Drainage Pump | N/A | Reset Hours Run Command | N/A | N/A | N/A
| OS | CIPDO | SMP172 | DPP321_SI.ResetHoursRunCmd | 1 | LGD | N/A | DPP_ | N/A | DPP321 | N/A | Tunnel Drainage Pump | N/A | Reset Hours Run Command | N/A | N/A | N/A
| OS | CIPDO | SMP172 | DPP321_SI.ResetHoursRunCmd | 2 | LGD | N/A | DPP_ | N/A | DPP321 | N/A | Tunnel Drainage Pump | N/A | Reset Hours Run Command | N/A | N/A | N/A
| OS | CIPDO | SMP172 | DPP321_SI.ResetHoursRunCmd | 3 | LGD | N/A | DPP_ | N/A | DPP321 | N/A | Tunnel Drainage Pump | N/A | Reset Hours Run Command | N/A | N/A | N/A
| OS | CIPDO | SMP172 | DPP321_SI.ResetHoursRunCmd | 4 | LGD | N/A | DPP_ | N/A | DPP321 | N/A | Tunnel Drainage Pump | N/A | Reset Hours Run Command | N/A | N/A | N/A
| OS | CIPDO | SMP172 | DPP321_SI.ResetHoursRunCmd | 5 | LGD | N/A | DPP_ | N/A | DPP321 | N/A | Tunnel Drainage Pump | N/A | Reset Hours Run Command | N/A | N/A | N/A
| OK | CIPDO | SMP172 | DPP321_SI.ResetHoursRunCmd | 6 | LGD | N/A | DPP_ | N/A | DPP321 | N/A | Tunnel Drainage Pump | N/A | Reset Hours Run Command | N/A | Reset | N/A
| OS | CIPDO | SMP172 | DPP321_SI.ResetHoursRunCmd | 7 | LGD | N/A | DPP_ | N/A | DPP321 | N/A | Tunnel Drainage Pump | N/A | Reset Hours Run Command | N/A | N/A | N/A
OK
| OS | CIPDO | SMP172 | DPP322_SI.AlarmResetCmd | 0 | LGD | N/A | DPP_ | N/A | DPP322 | N/A | Tunnel Drainage Pump | N/A | Alarm Reset Command | N/A | N/A | N/A
| OS | CIPDO | SMP172 | DPP322_SI.AlarmResetCmd | 1 | LGD | N/A | DPP_ | N/A | DPP322 | N/A | Tunnel Drainage Pump | N/A | Alarm Reset Command | N/A | N/A | N/A
| OS | CIPDO | SMP172 | DPP322_SI.AlarmResetCmd | 2 | LGD | N/A | DPP_ | N/A | DPP322 | N/A | Tunnel Drainage Pump | N/A | Alarm Reset Command | N/A | N/A | N/A
| OS | CIPDO | SMP172 | DPP322_SI.AlarmResetCmd | 3 | LGD | N/A | DPP_ | N/A | DPP322 | N/A | Tunnel Drainage Pump | N/A | Alarm Reset Command | N/A | N/A | N/A
| OS | CIPDO | SMP172 | DPP322_SI.AlarmResetCmd | 4 | LGD | N/A | DPP_ | N/A | DPP322 | N/A | Tunnel Drainage Pump | N/A | Alarm Reset Command | N/A | N/A | N/A
| OS | CIPDO | SMP172 | DPP322_SI.AlarmResetCmd | 5 | LGD | N/A | DPP_ | N/A | DPP322 | N/A | Tunnel Drainage Pump | N/A | Alarm Reset Command | N/A | N/A | N/A
| OK | CIPDO | SMP172 | DPP322_SI.AlarmResetCmd | 6 | LGD | N/A | DPP_ | N/A | DPP322 | N/A | Tunnel Drainage Pump | N/A | Alarm Reset Command | N/A | Reset | N/A
| OS | CIPDO | SMP172 | DPP322_SI.AlarmResetCmd | 7 | LGD | N/A | DPP_ | N/A | DPP322 | N/A | Tunnel Drainage Pump | N/A | Alarm Reset Command | N/A | N/A | N/A
OK
| OS | CIPDO | SMP172 | DPP322_SI.AvailabilityCmd | 0 | LGD | N/A | DPP_ | N/A | DPP322 | N/A | Tunnel Drainage Pump | N/A | Availability Command | N/A | N/A | N/A
| OS | CIPDO | SMP172 | DPP322_SI.AvailabilityCmd | 1 | LGD | N/A | DPP_ | N/A | DPP322 | N/A | Tunnel Drainage Pump | N/A | Availability Command | N/A | N/A | N/A
| OS | CIPDO | SMP172 | DPP322_SI.AvailabilityCmd | 2 | LGD | N/A | DPP_ | N/A | DPP322 | N/A | Tunnel Drainage Pump | N/A | Availability Command | N/A | N/A | N/A
| OS | CIPDO | SMP172 | DPP322_SI.AvailabilityCmd | 3 | LGD | N/A | DPP_ | N/A | DPP322 | N/A | Tunnel Drainage Pump | N/A | Availability Command | N/A | N/A | N/A
| OS | CIPDO | SMP172 | DPP322_SI.AvailabilityCmd | 4 | LGD | N/A | DPP_ | N/A | DPP322 | N/A | Tunnel Drainage Pump | N/A | Availability Command | N/A | N/A | N/A
| OK | CIPDO | SMP172 | DPP322_SI.AvailabilityCmd | 5 | LGD | N/A | DPP_ | N/A | DPP322 | N/A | Tunnel Drainage Pump | N/A | Availability Command | N/A | Out Of Service | N/A
| OK | CIPDO | SMP172 | DPP322_SI.AvailabilityCmd | 6 | LGD | N/A | DPP_ | N/A | DPP322 | N/A | Tunnel Drainage Pump | N/A | Availability Command | N/A | In Service | N/A
| OS | CIPDO | SMP172 | DPP322_SI.AvailabilityCmd | 7 | LGD | N/A | DPP_ | N/A | DPP322 | N/A | Tunnel Drainage Pump | N/A | Availability Command | N/A | N/A | N/A
OK
| OS | CIPDO | SMP172 | DPP322_SI.ControlModeCmd | 0 | LGD | N/A | DPP_ | N/A | DPP322 | N/A | Tunnel Drainage Pump | N/A | Control Mode Command | N/A | N/A | N/A
| OS | CIPDO | SMP172 | DPP322_SI.ControlModeCmd | 1 | LGD | N/A | DPP_ | N/A | DPP322 | N/A | Tunnel Drainage Pump | N/A | Control Mode Command | N/A | N/A | N/A
| OS | CIPDO | SMP172 | DPP322_SI.ControlModeCmd | 2 | LGD | N/A | DPP_ | N/A | DPP322 | N/A | Tunnel Drainage Pump | N/A | Control Mode Command | N/A | N/A | N/A
| OS | CIPDO | SMP172 | DPP322_SI.ControlModeCmd | 3 | LGD | N/A | DPP_ | N/A | DPP322 | N/A | Tunnel Drainage Pump | N/A | Control Mode Command | N/A | N/A | N/A
| OS | CIPDO | SMP172 | DPP322_SI.ControlModeCmd | 4 | LGD | N/A | DPP_ | N/A | DPP322 | N/A | Tunnel Drainage Pump | N/A | Control Mode Command | N/A | N/A | N/A
| OK | CIPDO | SMP172 | DPP322_SI.ControlModeCmd | 5 | LGD | N/A | DPP_ | N/A | DPP322 | N/A | Tunnel Drainage Pump | N/A | Control Mode Command | N/A | Remote Manual | N/A
| OK | CIPDO | SMP172 | DPP322_SI.ControlModeCmd | 6 | LGD | N/A | DPP_ | N/A | DPP322 | N/A | Tunnel Drainage Pump | N/A | Control Mode Command | N/A | Remote Auto | N/A
| OS | CIPDO | SMP172 | DPP322_SI.ControlModeCmd | 7 | LGD | N/A | DPP_ | N/A | DPP322 | N/A | Tunnel Drainage Pump | N/A | Control Mode Command | N/A | N/A | N/A
OK
| OS | CIPDO | SMP172 | DPP322_SI.OpStateCmd | 0 | LGD | N/A | DPP_ | N/A | DPP322 | N/A | Tunnel Drainage Pump | N/A | Operational State Command | N/A | N/A | N/A
| OS | CIPDO | SMP172 | DPP322_SI.OpStateCmd | 1 | LGD | N/A | DPP_ | N/A | DPP322 | N/A | Tunnel Drainage Pump | N/A | Operational State Command | N/A | N/A | N/A
| OS | CIPDO | SMP172 | DPP322_SI.OpStateCmd | 2 | LGD | N/A | DPP_ | N/A | DPP322 | N/A | Tunnel Drainage Pump | N/A | Operational State Command | N/A | N/A | N/A
| OS | CIPDO | SMP172 | DPP322_SI.OpStateCmd | 3 | LGD | N/A | DPP_ | N/A | DPP322 | N/A | Tunnel Drainage Pump | N/A | Operational State Command | N/A | N/A | N/A
| OS | CIPDO | SMP172 | DPP322_SI.OpStateCmd | 4 | LGD | N/A | DPP_ | N/A | DPP322 | N/A | Tunnel Drainage Pump | N/A | Operational State Command | N/A | N/A | N/A
| OK | CIPDO | SMP172 | DPP322_SI.OpStateCmd | 5 | LGD | N/A | DPP_ | N/A | DPP322 | N/A | Tunnel Drainage Pump | N/A | Operational State Command | N/A | Run | N/A
| OK | CIPDO | SMP172 | DPP322_SI.OpStateCmd | 6 | LGD | N/A | DPP_ | N/A | DPP322 | N/A | Tunnel Drainage Pump | N/A | Operational State Command | N/A | Stop | N/A
| OS | CIPDO | SMP172 | DPP322_SI.OpStateCmd | 7 | LGD | N/A | DPP_ | N/A | DPP322 | N/A | Tunnel Drainage Pump | N/A | Operational State Command | N/A | N/A | N/A