## Report
Overall Result | EventList Result | Data Type | Register | Register Offset | Triggering State | EQP number |  | Attribute description |  | State |  | EQP description |  | EQP code |  | Station |  | Alarm Severity
[6 empty] | Searched | Found | Searched | Found | Searched | Found | Searched | Found | Searched | Found | Searched | Found | Searched | Found
NOK
| NOK | DI | 20.0 | 0 | 1 | ECS-AHU-G-01 | ECS-ACS-02002 | On/Off Status | Fault | On | Alarm | Air Handling Unit | Air-Conditioning | AH1J | ACSJ | TAP | EA1 | 0.0 | 2.0
| NOK | DI | 20.0 | 0 | 0 | ECS-AHU-G-01 | ECS-ACS-02002 | On/Off Status | Fault | Off | Alarm | Air Handling Unit | Air-Conditioning | AH1J | ACSJ | TAP | EA1 | 0.0 | 2.0
OK
| OK | DI | 20.0 | 1.0 | 1 | ECS-AHU-G-01 | ECS-AHU-G-01 | Auto/Manual Status | Auto/Manual Status | Auto | Auto | Air Handling Unit | Air Handling Unit | AH1J | AH1J | TAP | TAP | 0.0 | 0.0
| OK | DI | 20.0 | 1.0 | 0 | ECS-AHU-G-01 | ECS-AHU-G-01 | Auto/Manual Status | Auto/Manual Status | Manual | Manual | Air Handling Unit | Air Handling Unit | AH1J | AH1J | TAP | TAP | 0.0 | 0.0
OK
| OK | DI | 20.0 | 2.0 | 1 | ECS-AHU-G-01 | ECS-AHU-G-01 | Fault Alarm | Fault Alarm | Alarm | Alarm | Air Handling Unit | Air Handling Unit | AH1J | AH1J | TAP | TAP | 2.0 | 2.0
| OK | DI | 20.0 | 2.0 | 0 | ECS-AHU-G-01 | ECS-AHU-G-01 | Fault Alarm | Fault Alarm | Normal | Normal | Air Handling Unit | Air Handling Unit | AH1J | AH1J | TAP | TAP | 0.0 | 0.0
OK
| OK | DI | 20.0 | 3.0 | 1 | ECS-AHU-L1-01 | ECS-AHU-L1-01 | On/Off Status | On/Off Status | On | On | Air Handling Unit | Air Handling Unit | AH1J | AH1J | TAP | TAP | 0.0 | 0.0
| OK | DI | 20.0 | 3.0 | 0 | ECS-AHU-L1-01 | ECS-AHU-L1-01 | On/Off Status | On/Off Status | Off | Off | Air Handling Unit | Air Handling Unit | AH1J | AH1J | TAP | TAP | 0.0 | 0.0
OK
| OK | DI | 20.0 | 4.0 | 1 | ECS-AHU-L1-01 | ECS-AHU-L1-01 | Auto/Manual Status | Auto/Manual Status | Auto | Auto | Air Handling Unit | Air Handling Unit | AH1J | AH1J | TAP | TAP | 0.0 | 0.0
| OK | DI | 20.0 | 4.0 | 0 | ECS-AHU-L1-01 | ECS-AHU-L1-01 | Auto/Manual Status | Auto/Manual Status | Manual | Manual | Air Handling Unit | Air Handling Unit | AH1J | AH1J | TAP | TAP | 0.0 | 0.0
OK
| OK | DI | 20.0 | 5.0 | 1 | ECS-AHU-L1-01 | ECS-AHU-L1-01 | Fault Alarm | Fault Alarm | Alarm | Alarm | Air Handling Unit | Air Handling Unit | AH1J | AH1J | TAP | TAP | 2.0 | 2.0
| OK | DI | 20.0 | 5.0 | 0 | ECS-AHU-L1-01 | ECS-AHU-L1-01 | Fault Alarm | Fault Alarm | Normal | Normal | Air Handling Unit | Air Handling Unit | AH1J | AH1J | TAP | TAP | 0.0 | 0.0
OK
| OK | DI | 20.0 | 6.0 | 1 | ECS-AHU-L1-02 | ECS-AHU-L1-02 | On/Off Status | On/Off Status | On | On | Air Handling Unit | Air Handling Unit | AH1J | AH1J | TAP | TAP | 0.0 | 0.0
| OK | DI | 20.0 | 6.0 | 0 | ECS-AHU-L1-02 | ECS-AHU-L1-02 | On/Off Status | On/Off Status | Off | Off | Air Handling Unit | Air Handling Unit | AH1J | AH1J | TAP | TAP | 0.0 | 0.0
OK
| OK | DI | 20.0 | 7.0 | 1 | ECS-AHU-L1-02 | ECS-AHU-L1-02 | Auto/Manual Status | Auto/Manual Status | Auto | Auto | Air Handling Unit | Air Handling Unit | AH1J | AH1J | TAP | TAP | 0.0 | 0.0
| OK | DI | 20.0 | 7.0 | 0 | ECS-AHU-L1-02 | ECS-AHU-L1-02 | Auto/Manual Status | Auto/Manual Status | Manual | Manual | Air Handling Unit | Air Handling Unit | AH1J | AH1J | TAP | TAP | 0.0 | 0.0
NOK
| NOK | DI | 20.0 | 8.0 | 1 | ECS-AHU-L1-02 | ECS-AHU-G-01 | Fault Alarm | On/Off | Alarm | Off | Air Handling Unit | Air Handling Unit | AH1J | AH1J | TAP | TAP | 2.0 | 0.0
| NOK | DI | 20.0 | 8.0 | 0 | ECS-AHU-L1-02 | ECS-AHU-G-01 | Fault Alarm | On/Off | Normal | On | Air Handling Unit | Air Handling Unit | AH1J | AH1J | TAP | TAP | 0.0 | 0.0
NOK
| NOK | DI | 20.0 | 9.0 | 1 | ECS-AHU-L1-03 | ECS-AHU-G-01 | On/Off Status | On/Off Status | On | Off | Air Handling Unit | Air Handling Unit | AH1J | AH1J | TAP | TAP | 0.0 | 0.0
| NOK | DI | 20.0 | 9.0 | 0 | ECS-AHU-L1-03 | ECS-AHU-G-01 | On/Off Status | On/Off Status | Off | On | Air Handling Unit | Air Handling Unit | AH1J | AH1J | TAP | TAP | 0.0 | 0.0
OK
| OK | DI2 | 40.0 | 0 | 1 | ECS-MSFD-001 | ECS-MSFD-001 | Status | Status | Close | Close | Motorised Smoke & Fire Damper | Motorised Smoke & Fire Damper | MFDJ | MFDJ | TAP | TAP | 0.0 | 0.0
| OK | DI2 | 40.0 | 0 | 2 | ECS-MSFD-001 | ECS-MSFD-001 | Status | Status | Open | Open | Motorised Smoke & Fire Damper | Motorised Smoke & Fire Damper | MFDJ | MFDJ | TAP | TAP | 0.0 | 0.0
| OK | DI2 | 40.0 | 0 | 3 | ECS-MSFD-001 | ECS-MSFD-001 | Status | Status | Fault | Fault | Motorised Smoke & Fire Damper | Motorised Smoke & Fire Damper | MFDJ | MFDJ | TAP | TAP | 2.0 | 2.0
| OK | DI2 | 40.0 | 0 | 0 | ECS-MSFD-001 | ECS-MSFD-001 | Status | Status | Transit | Transit | Motorised Smoke & Fire Damper | Motorised Smoke & Fire Damper | MFDJ | MFDJ | TAP | TAP | 0.0 | 0.0
OK
| OK | DI2 | 41.0 | 0 | 1 | ECS-MSFD-002 | ECS-MSFD-002 | Status | Status | Close | Close | Motorised Smoke & Fire Damper | Motorised Smoke & Fire Damper | MFDJ | MFDJ | TAP | TAP | 0.0 | 0.0
| OK | DI2 | 41.0 | 0 | 2 | ECS-MSFD-002 | ECS-MSFD-002 | Status | Status | Open | Open | Motorised Smoke & Fire Damper | Motorised Smoke & Fire Damper | MFDJ | MFDJ | TAP | TAP | 0.0 | 0.0
| OK | DI2 | 41.0 | 0 | 3 | ECS-MSFD-002 | ECS-MSFD-002 | Status | Status | Fault | Fault | Motorised Smoke & Fire Damper | Motorised Smoke & Fire Damper | MFDJ | MFDJ | TAP | TAP | 2.0 | 2.0
| OK | DI2 | 41.0 | 0 | 0 | ECS-MSFD-002 | ECS-MSFD-002 | Status | Status | Transit | Transit | Motorised Smoke & Fire Damper | Motorised Smoke & Fire Damper | MFDJ | MFDJ | TAP | TAP | 0.0 | 0.0
OK
| OK | DI2 | 42.0 | 0 | 1 | ECS-MSFD-003 | ECS-MSFD-003 | Status | Status | Close | Close | Motorised Smoke & Fire Damper | Motorised Smoke & Fire Damper | MFDJ | MFDJ | TAP | TAP | 0.0 | 0.0
| OK | DI2 | 42.0 | 0 | 2 | ECS-MSFD-003 | ECS-MSFD-003 | Status | Status | Open | Open | Motorised Smoke & Fire Damper | Motorised Smoke & Fire Damper | MFDJ | MFDJ | TAP | TAP | 0.0 | 0.0
| OK | DI2 | 42.0 | 0 | 3 | ECS-MSFD-003 | ECS-MSFD-003 | Status | Status | Fault | Fault | Motorised Smoke & Fire Damper | Motorised Smoke & Fire Damper | MFDJ | MFDJ | TAP | TAP | 2.0 | 2.0
| OK | DI2 | 42.0 | 0 | 0 | ECS-MSFD-003 | ECS-MSFD-003 | Status | Status | Transit | Transit | Motorised Smoke & Fire Damper | Motorised Smoke & Fire Damper | MFDJ | MFDJ | TAP | TAP | 0.0 | 0.0
OK
| OK | DI2 | 43.0 | 0 | 1 | ECS-MSFD-004 | ECS-MSFD-004 | Status | Status | Close | Close | Motorised Smoke & Fire Damper | Motorised Smoke & Fire Damper | MFDJ | MFDJ | TAP | TAP | 0.0 | 0.0
| OK | DI2 | 43.0 | 0 | 2 | ECS-MSFD-004 | ECS-MSFD-004 | Status | Status | Open | Open | Motorised Smoke & Fire Damper | Motorised Smoke & Fire Damper | MFDJ | MFDJ | TAP | TAP | 0.0 | 0.0
| OK | DI2 | 43.0 | 0 | 3 | ECS-MSFD-004 | ECS-MSFD-004 | Status | Status | Fault | Fault | Motorised Smoke & Fire Damper | Motorised Smoke & Fire Damper | MFDJ | MFDJ | TAP | TAP | 2.0 | 2.0
| OK | DI2 | 43.0 | 0 | 0 | ECS-MSFD-004 | ECS-MSFD-004 | Status | Status | Transit | Transit | Motorised Smoke & Fire Damper | Motorised Smoke & Fire Damper | MFDJ | MFDJ | TAP | TAP | 0.0 | 0.0